|  | ......................... pcs .............................. € .............................. € GEZE Slimchain 230V chain drive For daily ventilation at vertically installed inward- and outward opening bottom-hung, top-hung and side-hung leaves. Chain drive as a direct opener in 230 V version. The drive must be controlled via a micro-processor. The opening width and operating speed in ventilation mode can be programmed individually via software. The drive is equipped with electronic end position cut-off and overload protection and has electronically regulated soft start and soft stop. . Automatic switch-off when the end position is reached. Overload protection when opening and closing. Sealing via electronically defined pressure. Drive brackets and chain attachment allow quick and easy installation from the front. Technical data: Stroke: 200/300/500 and 800 mm Tensile force/pressure: 300 N/max. 200 N, depending on stroke Voltage: 230 V AC Current consumption: Ventilation (230 V) 0.3 A IP rating: IP30 Ambient temperature: -5 °C to +70 °C Power supply cable: 2 m*, optionally special length on request Version: ( ) Solo Type of installation: ( ) surface-mounted ( ) integrated into the profile Type of window: ( ) Bottom-hung leaf ( ) Top-hung leaf ( ) Side-hung leaf ( ) inward opening ( ) outward opening other types of leaf available on request Leaf dimensions: ........ mm width (min. 560 mm) ........ mm height (min. 400 mm, depending on the type of window, panel weight, stroke and type of installation) Leaf material: ( ) Wood ( ) Aluminium ( ) Plastic Opening width: ........ mm or max. ....... mm (to be completed by the bidder) Colour: ( ) EV1 ( ) white RAL 9016 ( ) according to RAL .......... Note: When used on bottom-hung leaves, we prescribe the use of separate safety scissors (2 pieces) for product liability reasons, e.g. GEZE safety scissors no. 35 or no. 60. |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € ( ) Safety scissors (2 pcs.) |
|  | ......................... pcs. .............................. € .............................. € ( ) Console set Slimchain type A (bottom-hung) ( ) Console set Slimchain type B (top-hung) ( ) Console set Slimchain type C (integrated) |
|  | ......................... pcs. .............................. € .............................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
|  | ......................... pcs. .............................. € .............................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing of hold-open systems (optional position) Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pcs. .............................. € .............................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |