|  | ......... pcs .................. € .................. € GEZE MBZ 300 N 48 K Modular bus emergency power control panel for smoke and heat extraction and ventilation. For controlling 24 V DC electric drives with a total current consumption of 48 ampere. The central control panel can be extended by - ventilator groups that can be variably combined with storagable priorities – - alarm groups that can be variably configured with priorities and dependencies on alarm lines - alarm lines - fire sections and allows flexible adaptation to on-site requirements. The fire sections can be programmed without software and thus make installation fast and easy. The control panel has 5 free slots for further modules and can thus be extended by: - vent groups (Drive Module DM) - alarm groups (Sensor Module SM) - alarm lines (Sensor Module SM) - wind direction dependant actuation Automatic charger for temperature-compensated charging with monitoring of the charging equipment Automatic switchover from mains to battery operation Emergency power supply with rechargeable battery 2 x 12 V for at least 72 hours First operating level on the individual modules All alarm chains are line monitored, thus offering high safety. Parameters can be set for a potential-free status contact per alarm group for alarm or fault. 1 alarm group with: Evaluating line-monitored alarm lines Connection of automatic alarms with line monitoring in - max. two separately reported lines - max. 10 alarms each Connection possibility for a line-monitored external potential-free contact e.g. fire alarm system Connection of SHEV buttons with line monitoring Inputs for vent switch Parameters can be set for switch properties for - central button or assigned - dead man or catch - automatic step - automatic ventilation Parameters can be set for a potential-free status contact for alarm or fault. Bus-linked and configurable through software Status indication for the module and the connected components via LEDs for high operating comfort during installation and servicing 6 vent groups DM Each vent group controls a maximum of 10 ampere switching current Status inputs for which parameters can be set - as inhibiting input for sequence control - as input for feedback of the end positions OPEN and CLOSED In connection with LED displays e.g. on the vent switch to indicate the window status "open" or "closed" for the vent group Parameters can be set for switch properties for - dead man or catch - automatic step - automatic ventilation Motor connection with line monitoring Supply to holding magnets possible Actuation of pressure gas generators Short-circuit proof through automotive flat fuse Bus-linked and configurable through software Direct actuation of the module via operating level on the module for convenient start-up Status indication for the module and the connected components via LEDs for high operating comfort during installation and servicing Connection possibilities: - Rain-wind actuation - Smoke detector and/or heat detector - FT 4 SHEV button - Vent switch with or without LED function display - Alarm input for external trigger (fire alarm central unit) - Optional: further alarm groups (SM) - Optional: further vent groups (DM) Technical data: Input voltage: 230 V AC Output voltage: 24 V DC +-5 % in normal operation Fire sections can also be programmed without software Integrated service interval display Enclosure rating: IP 54 Output current max. 48 A Built in accordance with EN12010-9 and 10 VdS certified (G 512004) Steel cabinet with two-way key bit lock, painted grey (RAL 7035) Width: 600 mm Height: 600 mm Depth: 250 mm |
| --- | --- |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 DM drive module For use in the GEZE MBZ 300 modular bus emergency power control panel For controlling 24 V DC electric drives 10 ampere switching current Status inputs for which parameters can be set - as inhibiting input for sequence control - as input for feedback of the end positions OPEN and CLOSED In connection with LED displays e.g. on the vent switch to indicate the window status "open" or "closed" for the vent group Parameters can be set for switch properties for - dead man or catch - automatic step - automatic ventilation Motor connection with line monitoring Supply to holding magnets possible Actuation of pressure gas generators Short-circuit proof through automotive flat fuse Bus-linked and configurable through software Direct actuation of the module via operating level on the module for convenient start-up Status indication for the module and the connected components via LEDs for high operating comfort during installation and servicing |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 DME drive module (extension) For use in the GEZE MBZ 300 modular bus emergency power control panel For controlling 24 V DC electric drives 20 ampere switching current Status inputs for which parameters can be set - as inhibiting input for sequence control - as input for feedback of the end positions OPEN and CLOSED In connection with LED displays e.g. on the vent switch to indicate the window status "open" or "closed" for the vent group Parameters can be set for switch properties for - dead man or catch - automatic step - automatic ventilation Motor connection with line monitoring Supply to holding magnets possible Actuation of pressure gas generators Short-circuit proof through automotive flat fuse Series terminals are required for drive connection Bus-linked and configurable through software Direct actuation of the module via operating level on the module for convenient start-up Status indication for the module and the connected components via LEDs for high operating comfort during installation and servicing |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 series terminals set For use in the GEZE MBZ 300 modular bus emergency power control panel For the connection of drives with larger cable diameter e.g. to the DME |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 SM sensor module For use in the GEZE MBZ 300 modular bus emergency power control panel For evaluating line-monitored alarm lines, formation of fire sections and ventilation control Connection of automatic alarms with line monitoring in - max. two separately reported lines - max. 10 each Connection of a line-monitored external potential-free contact e.g. fire alarm system Connection of SHEV buttons GEZE FT 4 with line monitoring Inputs for vent switch Parameters can be set for switch properties for - dead man or catch - automatic step - automatic ventilation Parameters can be set for a potential-free status contact for alarm or fault Bus-linked and configurable through software Status indication for the module and the connected components via LEDs for high operating comfort during installation and servicing |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 WM weather module For use in the emergency power control panel GEZE MBZ 300 For the automatic evaluation of weather sensors and / or for wind direction dependant actuation of smoke and heat extraction windows (natural SHEV) Possible components for different applications: GEZE rain / wind control with a potential-free contact for ventilation Rain sensor GC 401 RS and wind sensor GC 402 WVS for adjusting the max. wind speed for ventilation via the MBZ 300 software Rain sensor GC 401 RS and wind sensor GC 402 WVS and wind direction sensor GC 403 WDS as complete wind direction dependant actuation in accordance with EN 12101 Part 2 The settings are made using the MBZ 300 software. Status indication for the module and the connected components via LEDs for high operating comfort during installation and servicing |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 ERM relay module For use in the emergency power control panel GEZE MBZ 300 6 potential-free configurable status contacts for forwarding alarm, fault or ventilation signals The settings are made using the MBZ 300 software. Status indication for the module and the connected components via LEDs for high operating comfort during installation and servicing |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 CAN module For networking several MBZ 300 Every linked control panel needs a CAN module. Settings per MBZ 300 Software. Possibilities: superior alarm groups superior ventilation groups superior weather groups |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 PME power extension module For use in the GEZE MBZ 300 modular bus emergency power control panel For the extension of the overall current output Power supply status display via LED |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 PS 10 A power supply For use in the GEZE MBZ 300 modular bus emergency power control panel For the extension of the overall current output Output current 10 A |
|  | ......... pcs .................. € .................. € GEZE MBZ 300 power supply PS 24 A For use in the GEZE MBZ 300 modular bus emergency power control panel For the extension of the overall current output Output current 24 A |
|  | ......... pcs .................. € .................. € GEZE FT 4 K/24 V DC SHEV button for manual alarm triggering with alarm and reset key and LED display for "Fire alarm", "Operation", "Window open" and "Fault", in lockable surface-mounted housing marked "Smoke vent", with break glass pane, plastic housing in the colour: orange similar to RAL 2011 |
|  | ......... pcs .................. € .................. € GEZE FT4 A/24 V DC SHEV button – VdS for manual alarm triggering with alarm and reset button and LED display for "Fire alarm", "Operation", "Window open" and "Fault", in lockable surface-mounted housing marked "Smoke vent", with break glass pane, die-cast housing in the colour Colour: orange RAL 2011 (VdS approval) Alternatively: ( ) red RAL 3000 ( ) blue RAL 5015 ( ) yellow RAL 1021 ( ) grey RAL 7035 ( ) secondary unit, orange RAL 2011 (only with LED alarm) ( ) acoustic, orange RAL 2011 (with signal in the case of alarm, fault) |
|  | ......... pcs .................. € .................. € GEZE RM 1003/24 V DC for automatic alarm triggering in the case of smoke, VdS-approved version (G 205091) |
|  | ......... pcs .................. € .................. € GEZE WM 1005/24 V DC heat detector with base for automatic alarm triggering in the case of heat development, VdS-approved version (G 205092) |
|  | ......... pcs .................. € .................. € GEZE GC 162 RWA smoke detector with base Ceiling-mounted detector for automatically triggering an alarm in the case of smoke, simple testing using an integrated magnetic sensor, Tested in accordance with EN 54-7 |
|  | ......... pcs .................. € .................. € GEZE GC 163 RWA heat detector with base Ceiling-mounted detector for automatically triggering an alarm in the case of heat build-up, simple testing using an integrated magnetic sensor, Tested in accordance with EN 54-5 |
|  | ......... pcs .................. € .................. € GEZE vent switch for ventilation ( ) AS 500 vent switch LTA-24-AZ with function keys “Open-Close” and LED function display, enclosure rating IP 40, to match switch ranges with 55 x 55 mm switch insert, ( ) Surface-mounted ( ) Flush-mounted |
|  | ......... pcs .................. € .................. € GEZE E 70 room temperature regulator for automatic control of the room temperature. Adjustment of room temperature from 5 °C to 30 °C and switchover manual-automatic operation, (1 pcs.) |
|  | ......... pcs .................. € .................. € GEZE GC 240 RS rain sensor for the automatic closing of windows in case of rain in ventilation mode, rain sensor (heated electrically) with integrated control panel (1 piece) |
|  | ......... pcs .................. € .................. € GEZE rain/wind control for the automatic closing of windows in case of rain/wind in ventilation mode, consisting of weather station with rain and wind sensor (heated electrically), control panel (1 piece) |
|  | ......... pcs .................. € .................. € GEZE weather sensors Components: ( ) rain sensor GC 401 RS ( ) wind sensor GC 402 WVS ( ) wind direction sensor GC 403 WDS (rain and wind sensor necessary) For the automatic actuation for ventilation depending on rain and wind and / or for wind direction dependant actuation in case of a fire alarm (settings per MBZ 300 Software) REMARK Electrical cable routing and connection on site by an electrical contractor according to the GEZE cable diagrams. The type of cable to be used is to be determined with the respective local authorities. Configuration processes with the respective software can only be carried out by authorised persons. |
|  | ......... pcs .................. € .................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
|  | ......... pcs .................. € .................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
|  | ......... pcs .................. € .................. € Service maintenance - compact package Maintenance and testing of smoke and heat extraction systems (optional position) Service package for maintenance and testing according to ASR A1.6, DIN 18232 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
|  | ......... pcs .................. € .................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.6, DIN 18232 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......... pcs .................. € .................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |